## Impeller
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 12.7007 | 13.0468 | 148.1573 | 3.3948 | 1.6938 | 0.34619 |  |  | 11.3531 | 11.3531 | 2.2706 | -8.7363 |  | 0.0014285 | 0.33656 | 0.9 | 0.0047042 | 0 | 0 | Impeller | 0 | 0 | 0.33656 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 22.3674 | 29.5417 | 175.8438 | 3.9628 | 7.2244 | 7.1743 |  |  | 22.3173 | 22.3173 | 4.4635 | -10.6796 | 0.81211 | 0.037011 | 0.38929 | 0.9 | 0.10092 | 0 | 0 | Impeller | 0 | 0 | 0.38929 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 0.018524 | 0.48817 | 200.1881 | 2.8332 | -0.20925 | 0.46965 |  |  | 0.69743 | 0.69743 | 0.13949 | -0.088292 |  | 0.0026137 | 0.4331 | 0.9 | 0.0066997 | 0 | 0 | Impeller | 0 | 0 | 0.4331 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 0.013642 | 0.5186 | 226.0749 | 2.9203 | -0.20405 | 0.50496 |  |  | 0.72265 | 0.72265 | 0.14453 | -0.073164 |  | 0.0031731 | 0.47694 | 0.9 | 0.0073873 | 0 | 0 | Impeller | 0 | 0 | 0.47694 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 0.011286 | 0.53635 | 241.1756 | 2.9711 | -0.20102 | 0.52507 |  |  | 0.73737 | 0.73737 | 0.14747 | -0.064831 |  | 0.0035176 | 0.50134 | 0.9 | 0.007796 | 0 | 0 | Impeller | 0 | 0 | 0.50134 | 0.9 | 0 | 0 | 0 | 0 | 0
0.55 | [17 empty] | 0 | 0 | Impeller | 0
0.6 | 75.8385 | 243.9417 | 307.4741 | 7.3815 | 178.7237 | 168.1032 |  |  | 65.218 | 65.218 | 13.0436 | 115.9289 | 0.87959 | 1.4357 | 0.59667 | 0.9 | 2.6734 | 0 | 0 | Impeller | 0 | 0 | 0.59667 | 0.9 | 0 | 0 | 0 | 0 | 0
0.65 | 82.5915 | 248.957 | 326.4358 | 4.6958 | 207.2353 | 166.3655 |  |  | 41.7216 | 41.7216 | 8.3443 | 132.9882 | 0.92627 | 1.5085 | 0.62055 | 0.9 | 2.7008 | 170.9746 | 0.019518 | Impeller | 0.94934 | 461.7611 | 0.62055 | 0.9 | 395.083 | 66.6782 | 207.7925 | 177.7873 | 30.0052 | 0.1444
0.7 | 83.1101 | 247.887 | 347.8846 | 8.6962 | 210.4041 | 164.7769 |  |  | 37.4829 | 37.4829 | 7.4966 | 134.7907 | 0.93409 | 1.5921 | 0.64576 | 0.9 | 2.7393 | 270.5658 | 0.030887 | Impeller | 0.94934 | 741.1645 | 0.64576 | 0.9 | 634.1406 | 107.0239 | 333.524 | 285.3633 | 48.1608 | 0.1444
0.75 | 83.7315 | 245.9178 | 376.5345 | 14.7754 | 211.1716 | 162.1863 |  |  | 34.7462 | 34.7462 | 6.9492 | 134.3894 | 0.93791 | 1.6962 | 0.67654 | 0.9 | 2.7857 | 871.5673 | 0.099494 | Impeller | 0.94934 | 2427.9059 | 0.67654 | 0.9 | 2077.3171 | 350.5888 | 1092.5577 | 934.7927 | 157.765 | 0.1444
0.8 | 83.9642 | 243.5441 | 400.7648 | 10.7783 | 205.7693 | 159.5799 |  |  | 37.7748 | 37.7748 | 7.555 | 129.36 | 0.93091 | 1.7763 | 0.69986 | 0.9 | 2.82 | 592.3664 | 0.067622 | Impeller | 0.94934 | 1670.5025 | 0.69986 | 0.9 | 1429.2825 | 241.22 | 751.7261 | 643.1771 | 108.549 | 0.1444
0.85 | 81.9876 | 238.8713 | 423.7731 | 8.6324 | 199.9385 | 156.8837 |  |  | 38.9328 | 38.9328 | 7.7866 | 125.7375 | 0.92792 | 1.8466 | 0.71975 | 0.9 | 2.8506 | 579.126 | 0.06611 | Impeller | 0.94934 | 1650.8354 | 0.71975 | 0.9 | 1412.4554 | 238.3801 | 742.876 | 635.6049 | 107.271 | 0.1444
0.9 | 79.8409 | 233.5943 | 450.9589 | 15.4601 | 190.1726 | 153.7535 |  |  | 43.4217 | 43.4217 | 8.6843 | 119.0161 | 0.91559 | 1.9258 | 0.74043 | 0.9 | 2.8899 | 858.3269 | 0.097983 | Impeller | 0.94934 | 2480.4959 | 0.74043 | 0.9 | 2122.3131 | 358.1828 | 1116.2232 | 955.0409 | 161.1823 | 0.1444
0.95 | 79.6412 | 230.3686 | 475.9275 | 14.4342 | 180.5037 | 150.7275 |  |  | 49.8649 | 49.8649 | 9.973 | 110.8356 | 0.90002 | 1.9925 | 0.75671 | 0.9 | 2.9256 | 1837.5449 | 0.20977 | Impeller | 0.94934 | 5375.9888 | 0.75671 | 0.9 | 4599.6977 | 776.291 | 2419.1949 | 2069.864 | 349.331 | 0.1444
1 | 80.5548 | 228.3695 | 500.6074 | 15.0301 | 177.0767 | 147.8148 |  |  | 51.2929 | 51.2929 | 10.2586 | 106.7805 | 0.89514 | 2.0553 | 0.77023 | 0.9 | 2.9649 | 1685.5675 | 0.19242 | Impeller | 0.94934 | 4997.4843 | 0.77023 | 0.9 | 4275.8492 | 721.6351 | 2248.8679 | 1924.1321 | 324.7358 | 0.1444
1.05 | 80.6901 | 226.5418 | 517.5932 | 16.1365 | 163.381 | 145.8518 |  |  | 63.1608 | 63.1608 | 12.6322 | 95.3231 | 0.8657 | 2.0969 | 0.77812 | 0.9 | 2.9943 | 465.1429 | 0.053099 | Impeller | 0.94934 | 1392.7661 | 0.77812 | 0.9 | 1191.6512 | 201.115 | 626.7448 | 536.243 | 90.5017 | 0.1444
1.1 | 87.1753 | 229.7416 | 550.209 | 13.8392 | 204.2346 | 142.5662 |  |  | 25.507 | 25.507 | 5.1014 | 122.1607 | 0.94934 | 2.1788 | 0.78979 | 0.9 | 3.0652 | 54.1132 | 0.0061773 | Impeller | 0.94934 | 165.8694 | 0.78979 | 0.9 | 141.9179 | 23.9515 | 74.6412 | 63.8631 | 10.7782 | 0.1444
1.15 | 88.9823 | 230.1071 | 567.1194 | 15.13 | 205.6663 | 141.1248 |  |  | 24.4409 | 24.4409 | 4.8882 | 121.5721 | 0.95149 | 2.2231 | 0.79413 | 0.9 | 3.1104 | 0 | 0 | Impeller | 0 | 0 | 0.79413 | 0.9 | 0 | 0 | 0 | 0 | 0
1.2 | 91.77 | 227.9031 | 599.7249 | 10.5104 | 176.1535 | 136.1331 |  |  | 51.7497 | 51.7497 | 10.3499 | 94.7333 | 0.88042 | 2.2676 | 0.79902 | 0.9 | 3.1534 | 0 | 0 | Impeller | 0 | 0 | 0.79902 | 0.9 | 0 | 0 | 0 | 0 | 0
| 13.3771 | 13.7174 | 12.4892 | 5.1282 | 1.3217 | 0.3403 |  |  | 12.3957 | 12.3957 | 2.4791 | -9.5763 | 0.65126 | 0.0039211 | 0.030091 | 0.9 | 0.0068548 | 1374.7046 | 0.15693 | Impeller | 0.94934 | 9.4234 | 0.030091 | 0.9 | 8.0626 | 1.3607 | 4.2405 | 3.6282 | 0.61233 | 0.1444

## VSD
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 12.7007 | 13.0468 | 148.1573 | 3.3948 | 1.6938 | 0.34619 |  |  | 11.3531 | 11.3531 | 2.2706 | -8.7363 |  | 0.0014285 | 0.33656 | 0.9 | 0.0047042 | 0 | 0 | VSD | 0 | 0 | 0.33656 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 22.3674 | 29.5417 | 175.8438 | 3.9628 | 7.2244 | 7.1743 |  |  | 22.3173 | 22.3173 | 4.4635 | -10.6796 | 0.81211 | 0.037011 | 0.38929 | 0.9 | 0.10092 | 0 | 0 | VSD | 0 | 0 | 0.38929 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 0.018524 | 0.48817 | 200.1881 | 2.8332 | -0.20925 | 0.46965 |  |  | 0.69743 | 0.69743 | 0.13949 | -0.088292 |  | 0.0026137 | 0.4331 | 0.9 | 0.0066997 | 0 | 0 | VSD | 0 | 0 | 0.4331 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 0.013642 | 0.5186 | 226.0749 | 2.9203 | -0.20405 | 0.50496 |  |  | 0.72265 | 0.72265 | 0.14453 | -0.073164 |  | 0.0031731 | 0.47694 | 0.9 | 0.0073873 | 0 | 0 | VSD | 0 | 0 | 0.47694 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 0.011286 | 0.53635 | 241.1756 | 2.9711 | -0.20102 | 0.52507 |  |  | 0.73737 | 0.73737 | 0.14747 | -0.064831 |  | 0.0035176 | 0.50134 | 0.9 | 0.007796 | 0 | 0 | VSD | 0 | 0 | 0.50134 | 0.9 | 0 | 0 | 0 | 0 | 0
0.55 | [17 empty] | 0 | 0 | VSD | 0
0.6 | 75.8385 | 243.9417 | 307.4741 | 7.3815 | 178.7237 | 168.1032 |  |  | 65.218 | 65.218 | 13.0436 | 115.9289 | 0.87959 | 1.4357 | 0.59667 | 0.9 | 2.6734 | 0 | 0 | VSD | 0 | 0 | 0.59667 | 0.9 | 0 | 0 | 0 | 0 | 0
0.65 | 82.5915 | 248.957 | 326.4358 | 4.6958 | 207.2353 | 166.3655 |  |  | 41.7216 | 41.7216 | 8.3443 | 132.9882 | 0.92627 | 1.5085 | 0.62055 | 0.9 | 2.7008 | 170.9746 | 0.019518 | VSD | 0.92627 | 461.7611 | 0.62055 | 0.9 | 366.973 | 94.7881 | 207.7925 | 165.1379 | 42.6546 | 0.20528
0.7 | 83.1101 | 247.887 | 347.8846 | 8.6962 | 210.4041 | 164.7769 |  |  | 37.4829 | 37.4829 | 7.4966 | 134.7907 | 0.93409 | 1.5921 | 0.64576 | 0.9 | 2.7393 | 270.5658 | 0.030887 | VSD | 0.93409 | 741.1645 | 0.64576 | 0.9 | 604.0626 | 137.1019 | 333.524 | 271.8282 | 61.6959 | 0.18498
0.75 | 83.7315 | 245.9178 | 376.5345 | 14.7754 | 211.1716 | 162.1863 |  |  | 34.7462 | 34.7462 | 6.9492 | 134.3894 | 0.93791 | 1.6962 | 0.67654 | 0.9 | 2.7857 | 871.5673 | 0.099494 | VSD | 0.93791 | 2427.9059 | 0.67654 | 0.9 | 2003.1494 | 424.7565 | 1092.5577 | 901.4173 | 191.1404 | 0.17495
0.8 | 83.9642 | 243.5441 | 400.7648 | 10.7783 | 205.7693 | 159.5799 |  |  | 37.7748 | 37.7748 | 7.555 | 129.36 | 0.93091 | 1.7763 | 0.69986 | 0.9 | 2.82 | 592.3664 | 0.067622 | VSD | 0.93091 | 1670.5025 | 0.69986 | 0.9 | 1347.6334 | 322.8691 | 751.7261 | 606.435 | 145.2911 | 0.19328
0.85 | 81.9876 | 238.8713 | 423.7731 | 8.6324 | 199.9385 | 156.8837 |  |  | 38.9328 | 38.9328 | 7.7866 | 125.7375 | 0.92792 | 1.8466 | 0.71975 | 0.9 | 2.8506 | 579.126 | 0.06611 | VSD | 0.92792 | 1650.8354 | 0.71975 | 0.9 | 1318.9663 | 331.8691 | 742.876 | 593.5348 | 149.3411 | 0.20103
0.9 | 79.8409 | 233.5943 | 450.9589 | 15.4601 | 190.1726 | 153.7535 |  |  | 43.4217 | 43.4217 | 8.6843 | 119.0161 | 0.91559 | 1.9258 | 0.74043 | 0.9 | 2.8899 | 858.3269 | 0.097983 | VSD | 0.91559 | 2480.4959 | 0.74043 | 0.9 | 1903.8761 | 576.6198 | 1116.2232 | 856.7442 | 259.4789 | 0.23246
0.95 | 79.6412 | 230.3686 | 475.9275 | 14.4342 | 180.5037 | 150.7275 |  |  | 49.8649 | 49.8649 | 9.973 | 110.8356 | 0.90002 | 1.9925 | 0.75671 | 0.9 | 2.9256 | 1837.5449 | 0.20977 | VSD | 0.90002 | 5375.9888 | 0.75671 | 0.9 | 3919.3674 | 1456.6213 | 2419.1949 | 1763.7153 | 655.4796 | 0.27095
1 | 80.5548 | 228.3695 | 500.6074 | 15.0301 | 177.0767 | 147.8148 |  |  | 51.2929 | 51.2929 | 10.2586 | 106.7805 | 0.89514 | 2.0553 | 0.77023 | 0.9 | 2.9649 | 1685.5675 | 0.19242 | VSD | 0.89514 | 4997.4843 | 0.77023 | 0.9 | 3584.4683 | 1413.016 | 2248.8679 | 1613.0107 | 635.8572 | 0.28275
1.05 | 80.6901 | 226.5418 | 517.5932 | 16.1365 | 163.381 | 145.8518 |  |  | 63.1608 | 63.1608 | 12.6322 | 95.3231 | 0.8657 | 2.0969 | 0.77812 | 0.9 | 2.9943 | 465.1429 | 0.053099 | VSD | 0.8657 | 1392.7661 | 0.77812 | 0.9 | 903.6115 | 489.1546 | 626.7448 | 406.6252 | 220.1196 | 0.35121
1.1 | 87.1753 | 229.7416 | 550.209 | 13.8392 | 204.2346 | 142.5662 |  |  | 25.507 | 25.507 | 5.1014 | 122.1607 | 0.94934 | 2.1788 | 0.78979 | 0.9 | 3.0652 | 54.1132 | 0.0061773 | VSD | 0.94934 | 165.8694 | 0.78979 | 0.9 | 141.9179 | 23.9515 | 74.6412 | 63.8631 | 10.7782 | 0.1444
1.15 | 88.9823 | 230.1071 | 567.1194 | 15.13 | 205.6663 | 141.1248 |  |  | 24.4409 | 24.4409 | 4.8882 | 121.5721 | 0.95149 | 2.2231 | 0.79413 | 0.9 | 3.1104 | 0 | 0 | VSD | 0 | 0 | 0.79413 | 0.9 | 0 | 0 | 0 | 0 | 0
1.2 | 91.77 | 227.9031 | 599.7249 | 10.5104 | 176.1535 | 136.1331 |  |  | 51.7497 | 51.7497 | 10.3499 | 94.7333 | 0.88042 | 2.2676 | 0.79902 | 0.9 | 3.1534 | 0 | 0 | VSD | 0 | 0 | 0.79902 | 0.9 | 0 | 0 | 0 | 0 | 0
| 13.3771 | 13.7174 | 12.4892 | 5.1282 | 1.3217 | 0.3403 |  |  | 12.3957 | 12.3957 | 2.4791 | -9.5763 | 0.65126 | 0.0039211 | 0.030091 | 0.9 | 0.0068548 | 1374.7046 | 0.15693 | VSD | 0.65126 | 9.4234 | 0.030091 | 0.9 | 2.6029 | 6.8205 | 4.2405 | 1.1713 | 3.0692 | 0.72378