## Impeller
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | power_factor | motor_power | run_status | speed | motor_amp | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 10.6824 | 39.3467 | 194.987 | 15.5313 | 28.5394 | 0.92 | 450.7272 | 1.031 | 1534.9762 | 29.2071 | 28.6643 |  |  | 10.8073 | 10.8073 | 2.1615 | 20.0184 | 0.88724 | 0.15534 | 0.38829 | 0.9 | 0.44423 | 0 | 0 | Impeller | 0 | 0 | 0.38829 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 11.1227 | 41.303 | 220.2884 | 16.0767 | 32.4093 | 0.92 | 498.6332 | 1.0093 | 1628.7047 | 32.3114 | 30.1804 |  |  | 8.8938 | 8.8938 | 1.7788 | 23.0653 | 0.91135 | 0.18512 | 0.42834 | 0.9 | 0.47915 | 0 | 0 | Impeller | 0 | 0 | 0.42834 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 10.6729 | 44.6766 | 254.6733 | 17.4491 | 27.8288 | 0.92 | 574.2463 | 1.2433 | 1853.165 | 37.2111 | 34.0037 |  |  | 16.8478 | 16.8478 | 3.3696 | 20.5254 | 0.76856 | 0.24038 | 0.47909 | 0.9 | 0.55765 | 0 | 0 | Impeller | 0 | 0 | 0.47909 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 11.1566 | 51.259 | 287.3442 | 26.3491 | 34.2916 | 0.92 | 663.1014 | 1.4296 | 2124.9346 | 42.9689 | 40.1024 |  |  | 16.9675 | 16.9675 | 3.3935 | 26.5284 | 0.87115 | 0.3203 | 0.52327 | 0.9 | 0.67965 | 0 | 0 | Impeller | 0 | 0 | 0.52327 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 12.506 | 65.8723 | 326.0912 | 30.6311 | 30.5688 | 0.92 | 812.7433 | 1.87 | 2810.0661 | 52.6657 | 53.3662 |  |  | 35.3034 | 35.3034 | 7.0607 | 25.1235 | 0.77946 | 0.4845 | 0.57062 | 0.9 | 0.94186 | 45.1586 | 0.0051551 | Impeller | 0.88826 | 42.5331 | 0.57062 | 0.9 | 29.8088 | 12.7244 | 19.1399 | 13.4139 | 5.726 | 0.29916
0.55 | 11.2682 | 67.0307 | 357.9499 | 35.9632 | 32.6737 | 0.92 | 877.9151 | 1.9914 | 2950.4478 | 56.8888 | 55.7625 |  |  | 34.3571 | 34.3571 | 6.8714 | 28.2768 | 0.79668 | 0.5546 | 0.60544 | 0.9 | 1.0176 | 316.8755 | 0.036173 | Impeller | 0.88826 | 322.4481 | 0.60544 | 0.9 | 225.9834 | 96.4647 | 145.1017 | 101.6926 | 43.4091 | 0.29916
0.6 | 10.9165 | 66.173 | 392.5719 | 31.8223 | 31.4278 | 0.92 | 928.614 | 0.40371 | 2963.2284 | 60.1741 | 55.2565 |  |  | 34.7451 | 34.7451 | 6.949 | 27.4604 | 0.79192 | 0.60253 | 0.63894 | 0.9 | 1.0478 | 7222.3119 | 0.82446 | Impeller | 0.88826 | 7567.2401 | 0.63894 | 0.9 | 5303.3984 | 2263.8417 | 3405.2581 | 2386.5293 | 1018.7288 | 0.29916
0.65 | 12.8238 | 67.6596 | 408.877 | 45.8326 | 36.7409 | 0.92 | 937.0789 | 1.4865 | 2971.7288 | 60.7226 | 54.8358 |  |  | 30.9186 | 30.9186 | 6.1837 | 30.1009 | 0.8177 | 0.62269 | 0.65307 | 0.9 | 1.0594 | 953.6881 | 0.10887 | Impeller | 0.88826 | 1010.2912 | 0.65307 | 0.9 | 708.049 | 302.2422 | 454.6311 | 318.6221 | 136.009 | 0.29916
0.7 | 11.0524 | 65.2783 | 444.2965 | 59.5927 | 41.3626 | 0.92 | 977.9681 | 1.9999 | 2972.8658 | 63.3722 | 54.2259 |  |  | 23.9158 | 23.9158 | 4.7832 | 35.0933 | 0.86476 | 0.66923 | 0.6807 | 0.9 | 1.0923 | 159.2031 | 0.018174 | Impeller | 0.88826 | 173.8928 | 0.6807 | 0.9 | 121.8704 | 52.0224 | 78.2518 | 54.8417 | 23.4101 | 0.29916
0.75 | 10.1997 | 63.3379 | 472.6326 | 70.2008 | 43.4807 | 0.92 | 1004.4574 | 2 | 2975.3496 | 65.0887 | 53.1382 |  |  | 19.8572 | 19.8572 | 3.9714 | 37.2524 | 0.88826 | 0.69759 | 0.69951 | 0.9 | 1.108 | 62.7628 | 0.0071647 | Impeller | 0.88826 | 69.5427 | 0.69951 | 0.9 | 48.738 | 20.8046 | 31.2942 | 21.9321 | 9.3621 | 0.29916
0.8 | 8.2224 | 64.9089 | 502.0438 | 53.4081 | 40.0663 | 0.92 | 1080.7452 | 2 | 2971.2 | 70.0322 | 56.6865 |  |  | 24.8426 | 24.8426 | 4.9685 | 36.8124 | 0.86842 | 0.79023 | 0.71586 | 0.9 | 1.2266 | 0 | 0 | Impeller | 0 | 0 | 0.71586 | 0.9 | 0 | 0 | 0 | 0 | 0
0.85 | 11.9135 | 61.2182 | 542.5279 | 7.3808 | 26.0894 | 0.92 | 1051.8243 | 2 | 2960.0465 | 68.1581 | 49.3047 |  |  | 35.1287 | 35.1287 | 7.0257 | 21.2017 | 0.72667 | 0.74305 | 0.73313 | 0.9 | 1.1261 | 0 | 0 | Impeller | 0 | 0 | 0.73313 | 0.9 | 0 | 0 | 0 | 0 | 0
0.9 | [22 empty] | 0 | 0 | Impeller | 0
0.95 | [22 empty] | 0 | 0 | Impeller | 0
1 | [22 empty] | 0 | 0 | Impeller | 0
1.05 | [22 empty] | 0 | 0 | Impeller | 0
1.1 | [22 empty] | 0 | 0 | Impeller | 0
1.15 | [22 empty] | 0 | 0 | Impeller | 0

## VSD
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | power_factor | motor_power | run_status | speed | motor_amp | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 10.6824 | 39.3467 | 194.987 | 15.5313 | 28.5394 | 0.92 | 450.7272 | 1.031 | 1534.9762 | 29.2071 | 28.6643 |  |  | 10.8073 | 10.8073 | 2.1615 | 20.0184 | 0.88724 | 0.15534 | 0.38829 | 0.9 | 0.44423 | 0 | 0 | VSD | 0 | 0 | 0.38829 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 11.1227 | 41.303 | 220.2884 | 16.0767 | 32.4093 | 0.92 | 498.6332 | 1.0093 | 1628.7047 | 32.3114 | 30.1804 |  |  | 8.8938 | 8.8938 | 1.7788 | 23.0653 | 0.91135 | 0.18512 | 0.42834 | 0.9 | 0.47915 | 0 | 0 | VSD | 0 | 0 | 0.42834 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 10.6729 | 44.6766 | 254.6733 | 17.4491 | 27.8288 | 0.92 | 574.2463 | 1.2433 | 1853.165 | 37.2111 | 34.0037 |  |  | 16.8478 | 16.8478 | 3.3696 | 20.5254 | 0.76856 | 0.24038 | 0.47909 | 0.9 | 0.55765 | 0 | 0 | VSD | 0 | 0 | 0.47909 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 11.1566 | 51.259 | 287.3442 | 26.3491 | 34.2916 | 0.92 | 663.1014 | 1.4296 | 2124.9346 | 42.9689 | 40.1024 |  |  | 16.9675 | 16.9675 | 3.3935 | 26.5284 | 0.87115 | 0.3203 | 0.52327 | 0.9 | 0.67965 | 0 | 0 | VSD | 0 | 0 | 0.52327 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 12.506 | 65.8723 | 326.0912 | 30.6311 | 30.5688 | 0.92 | 812.7433 | 1.87 | 2810.0661 | 52.6657 | 53.3662 |  |  | 35.3034 | 35.3034 | 7.0607 | 25.1235 | 0.77946 | 0.4845 | 0.57062 | 0.9 | 0.94186 | 45.1586 | 0.0051551 | VSD | 0.77946 | 42.5331 | 0.57062 | 0.9 | 20.1421 | 22.391 | 19.1399 | 9.0639 | 10.076 | 0.52644
0.55 | 11.2682 | 67.0307 | 357.9499 | 35.9632 | 32.6737 | 0.92 | 877.9151 | 1.9914 | 2950.4478 | 56.8888 | 55.7625 |  |  | 34.3571 | 34.3571 | 6.8714 | 28.2768 | 0.79668 | 0.5546 | 0.60544 | 0.9 | 1.0176 | 316.8755 | 0.036173 | VSD | 0.79668 | 322.4481 | 0.60544 | 0.9 | 163.044 | 159.4041 | 145.1017 | 73.3698 | 71.7319 | 0.49436
0.6 | 10.9165 | 66.173 | 392.5719 | 31.8223 | 31.4278 | 0.92 | 928.614 | 0.40371 | 2963.2284 | 60.1741 | 55.2565 |  |  | 34.7451 | 34.7451 | 6.949 | 27.4604 | 0.79192 | 0.60253 | 0.63894 | 0.9 | 1.0478 | 7222.3119 | 0.82446 | VSD | 0.79192 | 7567.2401 | 0.63894 | 0.9 | 3758.2503 | 3808.9898 | 3405.2581 | 1691.2127 | 1714.0454 | 0.50335
0.65 | 12.8238 | 67.6596 | 408.877 | 45.8326 | 36.7409 | 0.92 | 937.0789 | 1.4865 | 2971.7288 | 60.7226 | 54.8358 |  |  | 30.9186 | 30.9186 | 6.1837 | 30.1009 | 0.8177 | 0.62269 | 0.65307 | 0.9 | 1.0594 | 953.6881 | 0.10887 | VSD | 0.8177 | 1010.2912 | 0.65307 | 0.9 | 552.376 | 457.9152 | 454.6311 | 248.5692 | 206.0618 | 0.45325
0.7 | 11.0524 | 65.2783 | 444.2965 | 59.5927 | 41.3626 | 0.92 | 977.9681 | 1.9999 | 2972.8658 | 63.3722 | 54.2259 |  |  | 23.9158 | 23.9158 | 4.7832 | 35.0933 | 0.86476 | 0.66923 | 0.6807 | 0.9 | 1.0923 | 159.2031 | 0.018174 | VSD | 0.86476 | 173.8928 | 0.6807 | 0.9 | 112.4508 | 61.442 | 78.2518 | 50.6028 | 27.6489 | 0.35333
0.75 | 10.1997 | 63.3379 | 472.6326 | 70.2008 | 43.4807 | 0.92 | 1004.4574 | 2 | 2975.3496 | 65.0887 | 53.1382 |  |  | 19.8572 | 19.8572 | 3.9714 | 37.2524 | 0.88826 | 0.69759 | 0.69951 | 0.9 | 1.108 | 62.7628 | 0.0071647 | VSD | 0.88826 | 69.5427 | 0.69951 | 0.9 | 48.738 | 20.8046 | 31.2942 | 21.9321 | 9.3621 | 0.29916
0.8 | 8.2224 | 64.9089 | 502.0438 | 53.4081 | 40.0663 | 0.92 | 1080.7452 | 2 | 2971.2 | 70.0322 | 56.6865 |  |  | 24.8426 | 24.8426 | 4.9685 | 36.8124 | 0.86842 | 0.79023 | 0.71586 | 0.9 | 1.2266 | 0 | 0 | VSD | 0 | 0 | 0.71586 | 0.9 | 0 | 0 | 0 | 0 | 0
0.85 | 11.9135 | 61.2182 | 542.5279 | 7.3808 | 26.0894 | 0.92 | 1051.8243 | 2 | 2960.0465 | 68.1581 | 49.3047 |  |  | 35.1287 | 35.1287 | 7.0257 | 21.2017 | 0.72667 | 0.74305 | 0.73313 | 0.9 | 1.1261 | 0 | 0 | VSD | 0 | 0 | 0.73313 | 0.9 | 0 | 0 | 0 | 0 | 0
0.9 | [22 empty] | 0 | 0 | VSD | 0
0.95 | [22 empty] | 0 | 0 | VSD | 0
1 | [22 empty] | 0 | 0 | VSD | 0
1.05 | [22 empty] | 0 | 0 | VSD | 0
1.1 | [22 empty] | 0 | 0 | VSD | 0
1.15 | [22 empty] | 0 | 0 | VSD | 0