## Impeller
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 12.7007 | 13.0468 | 148.1573 | 3.3948 | 1.6938 | 0.34619 |  |  | 11.3531 | 11.3531 | 2.2706 | -8.7363 |  | 0.0014285 | 0.33656 | 0.9 | 0.0047042 | 0 | 0 | Impeller | 0 | 0 | 0.33656 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 22.3674 | 29.5417 | 175.8438 | 3.9628 | 7.2244 | 7.1743 |  |  | 22.3173 | 22.3173 | 4.4635 | -10.6796 | 0.81211 | 0.037011 | 0.38929 | 0.9 | 0.10092 | 0 | 0 | Impeller | 0 | 0 | 0.38929 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 0.018524 | 0.48817 | 200.1881 | 2.8332 | -0.20925 | 0.46965 |  |  | 0.69743 | 0.69743 | 0.13949 | -0.088292 |  | 0.0026137 | 0.4331 | 0.9 | 0.0066997 | 0 | 0 | Impeller | 0 | 0 | 0.4331 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 0.013642 | 0.5186 | 226.0749 | 2.9203 | -0.20405 | 0.50496 |  |  | 0.72265 | 0.72265 | 0.14453 | -0.073164 |  | 0.0031731 | 0.47694 | 0.9 | 0.0073873 | 0 | 0 | Impeller | 0 | 0 | 0.47694 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 0.011286 | 0.53635 | 241.1756 | 2.9711 | -0.20102 | 0.52507 |  |  | 0.73737 | 0.73737 | 0.14747 | -0.064831 |  | 0.0035176 | 0.50134 | 0.9 | 0.007796 | 0 | 0 | Impeller | 0 | 0 | 0.50134 | 0.9 | 0 | 0 | 0 | 0 | 0
0.55 | [17 empty] | 0 | 0 | Impeller | 0
0.6 | 75.8385 | 243.9417 | 307.4741 | 7.3815 | 178.7237 | 168.1032 |  |  | 65.218 | 65.218 | 13.0436 | 115.9289 | 0.87959 | 1.4357 | 0.59667 | 0.9 | 2.6734 | 0 | 0 | Impeller | 0 | 0 | 0.59667 | 0.9 | 0 | 0 | 0 | 0 | 0
0.65 | 82.5915 | 248.957 | 326.4358 | 4.6958 | 207.2353 | 166.3655 |  |  | 41.7216 | 41.7216 | 8.3443 | 132.9882 | 0.92627 | 1.5085 | 0.62055 | 0.9 | 2.7008 | 202.7999 | 0.023151 | Impeller | 0.94934 | 547.7137 | 0.62055 | 0.9 | 468.624 | 79.0897 | 246.4712 | 210.8808 | 35.5904 | 0.1444
0.7 | 83.1101 | 247.887 | 347.8846 | 8.6962 | 210.4041 | 164.7769 |  |  | 37.4829 | 37.4829 | 7.4966 | 134.7907 | 0.93409 | 1.5921 | 0.64576 | 0.9 | 2.7393 | 320.9291 | 0.036636 | Impeller | 0.94934 | 879.1255 | 0.64576 | 0.9 | 752.18 | 126.9454 | 395.6065 | 338.481 | 57.1254 | 0.1444
0.75 | 83.7315 | 245.9178 | 376.5345 | 14.7754 | 211.1716 | 162.1863 |  |  | 34.7462 | 34.7462 | 6.9492 | 134.3894 | 0.93791 | 1.6962 | 0.67654 | 0.9 | 2.7857 | 1033.8015 | 0.11801 | Impeller | 0.94934 | 2879.8382 | 0.67654 | 0.9 | 2463.9905 | 415.8477 | 1295.9272 | 1108.7957 | 187.1315 | 0.1444
0.8 | 83.9642 | 243.5441 | 400.7648 | 10.7783 | 205.7693 | 159.5799 |  |  | 37.7748 | 37.7748 | 7.555 | 129.36 | 0.93091 | 1.7763 | 0.69986 | 0.9 | 2.82 | 702.63 | 0.080209 | Impeller | 0.94934 | 1981.4511 | 0.69986 | 0.9 | 1695.3302 | 286.1209 | 891.653 | 762.8986 | 128.7544 | 0.1444
0.85 | 81.9876 | 238.8713 | 423.7731 | 8.6324 | 199.9385 | 156.8837 |  |  | 38.9328 | 38.9328 | 7.7866 | 125.7375 | 0.92792 | 1.8466 | 0.71975 | 0.9 | 2.8506 | 686.9249 | 0.078416 | Impeller | 0.94934 | 1958.1232 | 0.71975 | 0.9 | 1675.3709 | 282.7524 | 881.1555 | 753.9169 | 127.2386 | 0.1444
0.9 | 79.8409 | 233.5943 | 450.9589 | 15.4601 | 190.1726 | 153.7535 |  |  | 43.4217 | 43.4217 | 8.6843 | 119.0161 | 0.91559 | 1.9258 | 0.74043 | 0.9 | 2.8899 | 1018.0965 | 0.11622 | Impeller | 0.94934 | 2942.2173 | 0.74043 | 0.9 | 2517.3621 | 424.8552 | 1323.9978 | 1132.813 | 191.1848 | 0.1444
0.95 | 79.6412 | 230.3686 | 475.9275 | 14.4342 | 180.5037 | 150.7275 |  |  | 49.8649 | 49.8649 | 9.973 | 110.8356 | 0.90002 | 1.9925 | 0.75671 | 0.9 | 2.9256 | 2179.5869 | 0.24881 | Impeller | 0.94934 | 6376.6795 | 0.75671 | 0.9 | 5455.889 | 920.7904 | 2869.5058 | 2455.1501 | 414.3557 | 0.1444
1 | 80.5548 | 228.3695 | 500.6074 | 15.0301 | 177.0767 | 147.8148 |  |  | 51.2929 | 51.2929 | 10.2586 | 106.7805 | 0.89514 | 2.0553 | 0.77023 | 0.9 | 2.9649 | 1999.3203 | 0.22823 | Impeller | 0.94934 | 5927.7198 | 0.77023 | 0.9 | 5071.759 | 855.9608 | 2667.4739 | 2282.2916 | 385.1824 | 0.1444
1.05 | 80.6901 | 226.5418 | 517.5932 | 16.1365 | 163.381 | 145.8518 |  |  | 63.1608 | 63.1608 | 12.6322 | 95.3231 | 0.8657 | 2.0969 | 0.77812 | 0.9 | 2.9943 | 551.725 | 0.062982 | Impeller | 0.94934 | 1652.0167 | 0.77812 | 0.9 | 1413.466 | 238.5507 | 743.4075 | 636.0597 | 107.3478 | 0.1444
1.1 | 87.1753 | 229.7416 | 550.209 | 13.8392 | 204.2346 | 142.5662 |  |  | 25.507 | 25.507 | 5.1014 | 122.1607 | 0.94934 | 2.1788 | 0.78979 | 0.9 | 3.0652 | 64.1858 | 0.0073271 | Impeller | 0.94934 | 196.7445 | 0.78979 | 0.9 | 168.3346 | 28.4098 | 88.535 | 75.7506 | 12.7844 | 0.1444
1.15 | 88.9823 | 230.1071 | 567.1194 | 15.13 | 205.6663 | 141.1248 |  |  | 24.4409 | 24.4409 | 4.8882 | 121.5721 | 0.95149 | 2.2231 | 0.79413 | 0.9 | 3.1104 | 0 | 0 | Impeller | 0 | 0 | 0.79413 | 0.9 | 0 | 0 | 0 | 0 | 0

## VSD
flowrate_percent | suction_pressure | discharge_pressure | discharge_flowrate | cv_opening | downstream_pressure | differential_pressure | actual_cv | calculated_cv_drop | measured_cv_drop | cv_pressure_drop | inherent_piping_loss | required_differential_pressure | required_speed_variation | base_hydraulic_power | old_pump_efficiency | old_motor_efficiency | base_motor_power | working_hours | working_percent | selected_option | selected_speed_variation | base_case_energy_consumption | new_pump_efficiency | new_motor_efficiency | proposed_case_energy_consumption | annual_energy_savings | base_case_emission | proposed_case_emission | ghg_reduction | ghg_reduction_percent
0.3 | 12.7007 | 13.0468 | 148.1573 | 3.3948 | 1.6938 | 0.34619 |  |  | 11.3531 | 11.3531 | 2.2706 | -8.7363 |  | 0.0014285 | 0.33656 | 0.9 | 0.0047042 | 0 | 0 | VSD | 0 | 0 | 0.33656 | 0.9 | 0 | 0 | 0 | 0 | 0
0.35 | 22.3674 | 29.5417 | 175.8438 | 3.9628 | 7.2244 | 7.1743 |  |  | 22.3173 | 22.3173 | 4.4635 | -10.6796 | 0.81211 | 0.037011 | 0.38929 | 0.9 | 0.10092 | 0 | 0 | VSD | 0 | 0 | 0.38929 | 0.9 | 0 | 0 | 0 | 0 | 0
0.4 | 0.018524 | 0.48817 | 200.1881 | 2.8332 | -0.20925 | 0.46965 |  |  | 0.69743 | 0.69743 | 0.13949 | -0.088292 |  | 0.0026137 | 0.4331 | 0.9 | 0.0066997 | 0 | 0 | VSD | 0 | 0 | 0.4331 | 0.9 | 0 | 0 | 0 | 0 | 0
0.45 | 0.013642 | 0.5186 | 226.0749 | 2.9203 | -0.20405 | 0.50496 |  |  | 0.72265 | 0.72265 | 0.14453 | -0.073164 |  | 0.0031731 | 0.47694 | 0.9 | 0.0073873 | 0 | 0 | VSD | 0 | 0 | 0.47694 | 0.9 | 0 | 0 | 0 | 0 | 0
0.5 | 0.011286 | 0.53635 | 241.1756 | 2.9711 | -0.20102 | 0.52507 |  |  | 0.73737 | 0.73737 | 0.14747 | -0.064831 |  | 0.0035176 | 0.50134 | 0.9 | 0.007796 | 0 | 0 | VSD | 0 | 0 | 0.50134 | 0.9 | 0 | 0 | 0 | 0 | 0
0.55 | [17 empty] | 0 | 0 | VSD | 0
0.6 | 75.8385 | 243.9417 | 307.4741 | 7.3815 | 178.7237 | 168.1032 |  |  | 65.218 | 65.218 | 13.0436 | 115.9289 | 0.87959 | 1.4357 | 0.59667 | 0.9 | 2.6734 | 0 | 0 | VSD | 0 | 0 | 0.59667 | 0.9 | 0 | 0 | 0 | 0 | 0
0.65 | 82.5915 | 248.957 | 326.4358 | 4.6958 | 207.2353 | 166.3655 |  |  | 41.7216 | 41.7216 | 8.3443 | 132.9882 | 0.92627 | 1.5085 | 0.62055 | 0.9 | 2.7008 | 202.7999 | 0.023151 | VSD | 0.92627 | 547.7137 | 0.62055 | 0.9 | 435.2817 | 112.432 | 246.4712 | 195.8767 | 50.5944 | 0.20528
0.7 | 83.1101 | 247.887 | 347.8846 | 8.6962 | 210.4041 | 164.7769 |  |  | 37.4829 | 37.4829 | 7.4966 | 134.7907 | 0.93409 | 1.5921 | 0.64576 | 0.9 | 2.7393 | 320.9291 | 0.036636 | VSD | 0.93409 | 879.1255 | 0.64576 | 0.9 | 716.5033 | 162.6222 | 395.6065 | 322.4265 | 73.18 | 0.18498
0.75 | 83.7315 | 245.9178 | 376.5345 | 14.7754 | 211.1716 | 162.1863 |  |  | 34.7462 | 34.7462 | 6.9492 | 134.3894 | 0.93791 | 1.6962 | 0.67654 | 0.9 | 2.7857 | 1033.8015 | 0.11801 | VSD | 0.93791 | 2879.8382 | 0.67654 | 0.9 | 2376.0172 | 503.821 | 1295.9272 | 1069.2078 | 226.7195 | 0.17495
0.8 | 83.9642 | 243.5441 | 400.7648 | 10.7783 | 205.7693 | 159.5799 |  |  | 37.7748 | 37.7748 | 7.555 | 129.36 | 0.93091 | 1.7763 | 0.69986 | 0.9 | 2.82 | 702.63 | 0.080209 | VSD | 0.93091 | 1981.4511 | 0.69986 | 0.9 | 1598.483 | 382.9682 | 891.653 | 719.3173 | 172.3357 | 0.19328
0.85 | 81.9876 | 238.8713 | 423.7731 | 8.6324 | 199.9385 | 156.8837 |  |  | 38.9328 | 38.9328 | 7.7866 | 125.7375 | 0.92792 | 1.8466 | 0.71975 | 0.9 | 2.8506 | 686.9249 | 0.078416 | VSD | 0.92792 | 1958.1232 | 0.71975 | 0.9 | 1564.4797 | 393.6435 | 881.1555 | 704.0159 | 177.1396 | 0.20103
0.9 | 79.8409 | 233.5943 | 450.9589 | 15.4601 | 190.1726 | 153.7535 |  |  | 43.4217 | 43.4217 | 8.6843 | 119.0161 | 0.91559 | 1.9258 | 0.74043 | 0.9 | 2.8899 | 1018.0965 | 0.11622 | VSD | 0.91559 | 2942.2173 | 0.74043 | 0.9 | 2258.2651 | 683.9523 | 1323.9978 | 1016.2193 | 307.7785 | 0.23246
0.95 | 79.6412 | 230.3686 | 475.9275 | 14.4342 | 180.5037 | 150.7275 |  |  | 49.8649 | 49.8649 | 9.973 | 110.8356 | 0.90002 | 1.9925 | 0.75671 | 0.9 | 2.9256 | 2179.5869 | 0.24881 | VSD | 0.90002 | 6376.6795 | 0.75671 | 0.9 | 4648.9215 | 1727.7579 | 2869.5058 | 2092.0147 | 777.4911 | 0.27095
1 | 80.5548 | 228.3695 | 500.6074 | 15.0301 | 177.0767 | 147.8148 |  |  | 51.2929 | 51.2929 | 10.2586 | 106.7805 | 0.89514 | 2.0553 | 0.77023 | 0.9 | 2.9649 | 1999.3203 | 0.22823 | VSD | 0.89514 | 5927.7198 | 0.77023 | 0.9 | 4251.684 | 1676.0358 | 2667.4739 | 1913.2578 | 754.2161 | 0.28275
1.05 | 80.6901 | 226.5418 | 517.5932 | 16.1365 | 163.381 | 145.8518 |  |  | 63.1608 | 63.1608 | 12.6322 | 95.3231 | 0.8657 | 2.0969 | 0.77812 | 0.9 | 2.9943 | 551.725 | 0.062982 | VSD | 0.8657 | 1652.0167 | 0.77812 | 0.9 | 1071.8105 | 580.2062 | 743.4075 | 482.3147 | 261.0928 | 0.35121
1.1 | 87.1753 | 229.7416 | 550.209 | 13.8392 | 204.2346 | 142.5662 |  |  | 25.507 | 25.507 | 5.1014 | 122.1607 | 0.94934 | 2.1788 | 0.78979 | 0.9 | 3.0652 | 64.1858 | 0.0073271 | VSD | 0.94934 | 196.7445 | 0.78979 | 0.9 | 168.3346 | 28.4098 | 88.535 | 75.7506 | 12.7844 | 0.1444
1.15 | 88.9823 | 230.1071 | 567.1194 | 15.13 | 205.6663 | 141.1248 |  |  | 24.4409 | 24.4409 | 4.8882 | 121.5721 | 0.95149 | 2.2231 | 0.79413 | 0.9 | 3.1104 | 0 | 0 | VSD | 0 | 0 | 0.79413 | 0.9 | 0 | 0 | 0 | 0 | 0